## Metrics
Metric Name | Metric Description | Metric Address | Metric Size | Scaling Factor | Data Type | Topic Name Suffix
Voltage_AN | 1s Phase A-N Voltage | 179 | 2 | 1.5259e-05 | INT32 | /nexus_meter/Voltage_AN
Voltage_BN | 1s Phase B-N Voltage | 181 | 2 | 1.5259e-05 | INT32 | /nexus_meter/Voltage_BN
Voltage_CN | 1s Phase C-N Voltage | 183 | 2 | 1.5259e-05 | INT32 | /nexus_meter/Voltage_CN
Current_N | 1s Neutral Current (Secondary) | 193 | 2 | 1.5259e-05 | INT32 | /nexus_meter/Current_N
VA | 1s Three Phase Apparent Power (Secondary) | 209 | 2 | 1.5259e-05 | INT32 | /nexus_meter/VA
VAR | 1s Three Phase Reactive Power (Secondary) | 217 | 2 | 1.5259e-05 | INT32 | /nexus_meter/VAR
W_A | 1s Phase A Active Power (Secondary) | 219 | 2 | 1.5259e-05 | INT32 | /nexus_meter/W_A
W_B | 1s Phase B Active Power (Secondary) | 221 | 2 | 1.5259e-05 | INT32 | /nexus_meter/W_B
W_C | 1s Phase C Active Power (Secondary) | 223 | 2 | 1.5259e-05 | INT32 | /nexus_meter/W_C
W | 1s Three Phase Active Power (Secondary) | 225 | 2 | 1.5259e-05 | INT32 | /nexus_meter/W
freq | 1s Frequency | 227 | 2 | 1.5259e-05 | INT32 | /nexus_meter/freq
pf_A | 1s Phase A Power Factor | 229 | 1 | 0.001 | UINT16 | /nexus_meter/pf_A
pf_B | 1s Phase B Power Factor | 230 | 1 | 0.001 | UINT16 | /nexus_meter/pf_B
pf_C | 1s Phase C Power Factor | 231 | 1 | 0.001 | UINT16 | /nexus_meter/pf_C
pf | 1s Three Phase Power Factor | 232 | 1 | 0.001 | UINT16 | /nexus_meter/pf
Angle_V_AN | 1s Phase A-N Voltage Angle | 2594 | 1 | 0.01 | INT16 | /nexus_meter/Angle_V_AN
Angle_V_BN | 1s Phase B-N Voltage Angle | 2595 | 1 | 0.01 | INT16 | /nexus_meter/Angle_V_BN
Angle_V_CN | 1s Phase C-N Voltage Angle | 2596 | 1 | 0.01 | INT16 | /nexus_meter/Angle_V_CN
Angle_I_A | 1s Phase A Current Angle | 2597 | 1 | 0.01 | INT16 | /nexus_meter/Angle_I_A
Angle_I_B | 1s Phase B Current Angle | 2598 | 1 | 0.01 | INT16 | /nexus_meter/Angle_I_B
Angle_I_C | 1s Phase C Current Angle | 2599 | 1 | 0.01 | INT16 | /nexus_meter/Angle_I_C